Objective :

1-to study and the performance of the power plant

2- To perform 1st and 2nd law analysis for the cycle.

Start-up Procedure

- Run the boiler and operate the burner. One hour is required to reach normal operating conditions of the boiler.

- Operate the steam turbine. Enough time is needed for warming the turbine before it is connected to the electrical generator.

- Run the vacuum pump and the circulating water pump which will circulate the water in the pipes.

- The experiment now is ready to carry on.

Experimental Procedure

- Perform the start-up procedure.

- Wait until readings reach steady state, and then start recording the temperatures (T1, T2, T3, T3’ ,T4), the boiler pressure, the condenser pressure, the mass flow rate of the steam , the mass flow rate of the cooling water and its inlet and outlet temperatures , the voltage and the current supplied by the electrical generator, the torque and the speed of the electrical generator, the amount of fuel consumed, and the time it took to consume that amount of fuel.   Given Data

- Atmospheric pressure  Patm = 100 kPa

- Atmospheric temperature Tatm = 15 oC

- Assume furnace temperature to be 1300 oC

Data observed

Table (1) :Data Observed

| Device/Location | Item | Unit | Value |
| --- | --- | --- | --- |
| Diesel Fuel | Consumed | mL | 800 |
|  | Time | s | 150 |
|  | Density | Kg/m3 | 750 |
|  | Calorific Value | kJ/kg | 41000 |
| Steam Generator | Feed Water Temperature | oC | 32 |
|  | Steam Temperature | oC | 285 |
|  | Boiler Pressure | Bar_Abs | 10 |
|  | Mass flow Rate | kg/hr | 150 |
| Steam Turbine | Inlet | oC | 275 |
|  | Outlet | oC | 75 |
| Steam Condenser | Inlet | oC | 70 |
|  | Condensate | oC | 30 |
|  | Pressure | bar_Abs | 0.10 |
| Cooling Tower | Flow rate | m3/hr | 15 |
|  | Inlet | oC | 17 |
|  | Outlet | oC | 23 |
| Electrical Generator | Voltage | Volts | 220 |
|  | Current | Ampere | 11 |
|  | Torque | N.m | 10 |
|  | Speed | Rpm | 3000 |

Sample Calculations  :

State 1 : Subcooled liquid

T1 = 30 C

P1 = 10 kPa

h1 = hf@30 C= 125.74 kJ/kg

s1 = sf@30 C = 0.4368 kJ/K.kg

𝑣1 = 𝑣𝑓 = 0.001004 m3 /kg

State 2 : Subcooled

T2 = 32 C

P2 = 10.5 bar ,

h2a = 134.99843 kJ/kg

State 3 : Superheated

T3 = 285 C

P3 = 10 bar

h3 = 3019.4 kJ/kg

s3 = 7.06750 kJ/K.kg

State 3* : Superheated

T3* = 275 C

P3* = 10 bar

h3* = 2997.57 kJ/kg

s3* = 7.02845 kJ/K.kg

State 4 : Superheated

T4 = 275 C

P4 = 10 bar

h4 = 2630.3 kJ/kg

s4 = 8.2891 kJ/K.kg

Step (2) : Take the steam generator as control volume and find 𝑄̇ 𝐻,𝑄̇ 𝑖𝑛 , ηS.G

𝑄̇H= 𝜌𝑓∀𝑓 𝑡 × 𝑄𝑐𝑣 × ηc = 750×800×10−6 150 × 41000 × 1 = 164 kW

𝑄̇in = 𝑚̇ 𝑠 × (ℎ3 − ℎ2 ) = 150 3600 × (3019.4 − 134.99843) = 120.183 kW

ηS.G = 𝑄̇ 𝑖𝑛 𝑄̇𝐻 = 120.183 164 × 100% = 73.28%

Step(3) : Take the steam turbine as control volume and find the following

The power delivered by the turbine 𝑊̇ 𝑇 = 𝑚̇ 𝑠 × (ℎ3 ′ − ℎ4 ) = 150 3600 × (2997.75 − 2630.3) = 15.31 kW

The power delivered to coupling = 𝑊̇r

The power delivered to electrical generator = 𝑊̇𝑔 𝑖𝑛 = 𝜏 × 𝜔 = 𝜏 × (2𝜋 𝑁/ 60) /1000 = 10 × 2𝜋* 3000 *60/ 1000 = 3.1416 kW

The electrical power generated𝑊̇E= 𝑉×𝐼 1000 = 220*11 / 1000 = 2.42 kW

ηcoupling = 𝑊̇ 𝑔 𝑖𝑛 𝑊̇ 𝑇 = (3.1416 /15.31) × 100% = 20.52%

ηgen    = 𝑊̇E /𝑊̇𝑔 𝑖𝑛 = (2.42 /3.1416) × 100% = 77.03%

Step(3) : Take the cooling system as control volume and find 𝑄̇𝐿 ,𝑄̇𝑐𝑤 , ηCond

𝑄̇l = 𝑚̇ 𝑠 × (ℎ4 − ℎ1 ) = (150 /3600) × (2630.3 − 125.74) = 104.356 kW

𝑄̇𝑐𝑤 = 𝑚̇ 𝑐𝑤 × 𝐶𝑝,𝑐𝑤 × ∆𝑇 = (15 ×1000 / 3600) × 4.18 × (23 − 17) = 104.5 kW

ηCond = 𝑄̇ 𝑐𝑤 𝑄̇𝐿 = 104.5 104.356 × 100% = 100.1%

Step(4) : Calculate the power consumed by the pump 𝑊̇ 𝑝, the net power of the cycle 𝑊̇ 𝑛𝑒𝑡and the thermal efficiency of the cycle ηth

W 𝑝 = 𝑚̇ 𝑠 × (ℎ2 − ℎ1 ) = (150 /3600) × (134.99843 − 125.74) = 0.3858 kW

𝑊̇net = 𝑊̇T − 𝑊̇P = 15.31 − 0.3858 = 14.924 kW

ηth = 𝑊̇𝑛𝑒𝑡 / 𝑄̇𝑖𝑛 = (14.924 /120.183) × 100% = 12.42 %

Step(5) : Calculate the Carnot thermal efficiency ηCarnot and the 2nd law efficiency of the cycle ηII

ηCarnot = 1- (𝑇𝐿/ 𝑇H) = 1 – (15+273 /1300+273) = 81.7%

ηII = ηth/ ηCarnot = (12.42%/ 81.7%) × 100% = 15.2 %

Step(5) : Calculate the rate of exergy destroyed in the processes 3’- 4 and 2-3

𝑋̇𝑑𝑒𝑠𝑡 3 *−4 = 𝑚̇ 𝑠𝑇𝑜 [𝑠4 − 𝑠3* ] =( 150 / 3600) × (15 + 273) × (8.2891 − 7.02845) = 15.1278 kW

𝑋̇𝑑𝑒𝑠𝑡 2−3 = 𝑚̇𝑠𝑇𝑜 [𝑠3 − 𝑠2 − 𝑞𝑖𝑛 𝑇𝐻 ] = (150 /3600) × (15 + 2730) (7.0675 − 0.463782 −                  2884.40157/ 1300+273 ) = 57.264 kW

Results & Discussion:

A steam power plant cycle is a cycle in which heat energy is converted into electrical energy. Since the objective of this experiment is to study the performance of a steam power plant cycle, several conclusions can be drawn from the results obtained from calculations. Firstly, the efficiency of the steam generator is 72.28% .This value means that 0.7228 of the heat energy resulting from the combustion of the fuel is absorbed by the working fluid , while the rest is dissipated as heat losses. Secondly, the efficiency of the electrical generator is 77.03%. This value means that 0.7703 of the power delivered to the generator can be used as electrical power, while the rest of the power was dissipated due to frictional losses. Thirdly, it is obvious that the efficiency of the condenser is 100.1%,which means that the cooling water in the condenser is absorbing heat from the working fluid in the cycle and the ambient air. Regarding the 2nd  law efficiency of the cycle , it can be concluded that the performance of this cycle is not good, since the efficiency of this cycle is only 15.2% of the most efficient ideal Carnot cycle. Finally, it is noticeable that the exergy destroyed in the process 2-3 is greater than the corresponding value in the process 3’-4 because of the heat transferred in that process Sources of Error Errors in this experiment are caused by several factors such as: human error in recording the experimental data and computational. In addition , since the unit used in the experiment is old established, errors from the measuring devices are possible.

Summery & Conclusions:

Overall, the experiment shows that steam power plant cycle are cycle that generates power using heat energy.. Frictional and heat losses dissipate most of the useful energy, which causes a reduction in the efficiency of the steam generator , the steam turbine and the efficiency of the whole cycle.